## Slide 1: Hydronic Heating/Cooling System of Intelligent Workplace at Carnegie Mellon University, Pittsburgh

## Slide 2: Components of the Hydronic of the heating/cooling system
Water Mullions System
Radiant Panels
Cool Waves

## Slide 3: IW Overall HVAC System
View of the basement heat exchanger
View of the supply/return pipes

## Slide 4: IW Schematic Hot Water System
Heat exchanger
Hot water pump to the fourth floor
* Only one pump is functional at any given time
Water flow rate sensor
Hot water supply/return temperature sensor

## Slide 5: IW Schematic Chilled Water System
Chilled water system flow rate valve
Chilled water system temperature sensor

## Slide 6: Secondary Water Loop in the 4th floor Mechanical room
Water mullion mixing valve
Water Mullion flow rate valve
Water mullion flow rate sensor

## Slide 7: HVAC Control System
Temperature of the hot water in the basement – 180 F
Temperature of the chilled water in the basement – 40-42 F
Temperature of the hot water on the 4th floor– 120 F
Mullion Surface Temperature – 80-90 F
Siemens control panel in the basement

## Slide 8: HVAC Control System
Johnson Controls – Metasys server (former)
Siemens Controls – Apogee server (March/April 2011)
The control system turns on the basement pump if the average south and north zone indoor temperature is below pump set-point (60 F) or if the schedule call for it which also turns on the fourth floor mullion water pump

## Slide 9: HVAC Control System
EN 1
Flow rate control
EN 2
EN 3
EN 4
EN 5
Temperature control
Actuator control
Flow rate control
Flow rate control
Temperature control
Actuator control
Actuator control
Temperature control
Siemens Apogee Server
Flow rate control
Temperature control
Actuator control
Flow rate control
Temperature control
Actuator control

## Slide 10: Mathematical model for the control system
Hot water set point equation:
Thws = (38-To)*foA + (72 – (Tsouth + Tnorth)/2) * fIA +120
Thws - Hot water supply temperature set point
Tnorth & south – indoor temperature of south/north zones
foA & fIA – outside/inside air temperature weighing factors (1)
Mullion surface temperature set point:
T mullion-s =((Tsouth +Tnorth)/2 + Thws)/2
T mullion-s- Mullion Surface temperature set-point

## Slide 11: Mullions - Heating/Cooling

## Slide 12: Mullions - Heating/Cooling
Supply water temperature sensor
Return water temperature sensor

## Slide 13: Mullions – Heating/Cooling
26 groups of mullions in the IW
Each group has four mullions controlled by one control valve/ flow rate meter
The mullion pump runs at 24 gpm during daytime schedule

## Slide 14: Performance Analysis of South Mullions for two days
Chart: Performance Analysis of South Mullion for two given days

## Slide 15: Radiant Panels
Sentra Flow rate valve
Radiant panel temperature sensor

## Slide 16: Radiant Panels
Water Supply to the radiant panels
Radiant Panels
Water Supply to the radiant panels

## Slide 17: Performance Analysis
Temperatures in the basement, IW mechanical room, mullion surface, radiant panel, cool wave
Flow rates at the basement, IW mechanical room, before/after supply/return
Temperature, humidity, CO2 measures
Entire system on/off controls
Night set back temperatures
Outdoor air temperature every 10 mins

## Slide 18: Performance Analysis of Radiant Panel 1 on two days
Chart: Performance Analysis of radiant Panel 1 for two given days

## Slide 19: Cool Waves – Cooling System

## Slide 20: Cool Waves – Cooling System
View of the LTG Cool Wave
Oscillating fans for air circulation
Air circulation by convection

## Slide 21: Implementation of web-based database
Import data from Csv file
Create the table of the database
Creating online database

## Slide 22: Implementation of web-based database
online database
PHP
Mullion ID | 1 | 2
04:00~05:00 | data1 | data2
05:00~06:00 | data3 | data4
12:00~13:00 | data N | Data N+1
Web Browser
…
JavaScript CSS
Web browser with GUI and analytic algorithm

## Slide 23: Mockup website